| SUBJECT* | 666 - Backflow Preventer Testing and Repair Service |
| --- | --- |

GENERAL INFORMATION

| CONTRACTING OFFICE’S ZIP CODE* | 80111 |
| --- | --- |
| SOLICITATION NUMBER* | 36C25926Q0177 |
| RESPONSE DATE/TIME/ZONE | 01-27-2026 14:00 MOUNTAIN TIME, DENVER, USA |
| ARCHIVE | 60 DAYS AFTER THE RESPONSE DATE |
| RECOVERY ACT FUNDS | N |
| SET-ASIDE | SDVOSBC |
| PRODUCT SERVICE CODE* | J045 |
| NAICS CODE* | 238220 |
| CONTRACTING OFFICE ADDRESS | Department of Veterans Affairs Network Contracting Office NCO 19 6162 South Willow Drive, Suite 300 Greenwood Village CO 80111 |
| POINT OF CONTACT* | Contracting Officer Danielle Kramer danielle.kramer@va.gov 303-712-5725 |

PLACE OF PERFORMANCE

| ADDRESS | Sheridan WY Medical Center |
| --- | --- |
|  | 1898 Fort Road |
|  | Sheridan WY |
| POSTAL CODE | 82801 |
| COUNTRY | USA |

ADDITIONAL INFORMATION

| AGENCY’S URL |  |
| --- | --- |
| URL DESCRIPTION |  |
| AGENCY CONTACT’S EMAIL ADDRESS |  |
| EMAIL DESCRIPTION |  |

DESCRIPTION

Backflow Preventer Testing and Repair Service

Question and Answers

Question 1: Can the Government provide a breakdown of the number and type of backflow assemblies per building and specifically how many devices are located at the Gillette VA Clinic?

Answer: Refer to attachment “Backflow Survey Oct2025” is the survey completed in October. There are two devices located in Gillette, One Reduced Pressure, one Double Check.

Question 2: Would a licensed plumber be acceptable to perform repairs when needed, provided repairs are completed under the supervision of or in conjunction with an ASSE 5130 technician?

Answer: No, the individual completing the repairs on site is required to carry the certification. Individuals will provide the certifications when arriving on site.

Question 3: Are any of the reduced pressure (RP) devices associated with fire suppression systems, or are they strictly for domestic/process water systems?

Answer: These are strictly domestic water supply.

Question 4: Are there any photos or drawings available that show the backflow device locations and setups?

Answer: Refer to attachment “Backflow Survey Oct2025” for location. Pictures are not available.

Question 5: Is this a service- disabled veteran set aside? Also, did the last contract go full term? Was the last contract dissolved early?

Answer: Yes, this requirement is a total SDVOSB set-aside as identified on page 1 in the “Set-Aside” section and Section IV on page 2. It was determined that it is in the best interest of the government to issue a new solicitation for this requirement. The phrase “dissolved early” is not a contracting term but it is assumed it is being asked if the current contract was terminated, it was not.

Question 6: Will contractor be required to move furniture, ceiling tile, and wall grates?

Answer: The Backflow devices are located in mechanical rooms once located they will be accessible without removing panels.

Question 7: What is the size of the devices?

Answer: Various sizes from ½” to 4”.

Question 8: Are all devices located on the floor or running in ceiling?

Answer: Various heights. Some floor level, some chest level, some overhead.

Question 9: Can the VA please provide the manufacturer, size, and model number for each of the backflow devices?

Answer: Refer to attachment “Backflow Survey Oct2025”, it has the known and unknown manufacturers and if the sizes are known.

Question 10: Do all of the backflow devices have isolation valves on both the upstream and downstream side to allow repairs to be made to the devices?

Answer: Yes, all the backflow preventers have isolation valves upstream and downstream of the devices.

Question 11: With regards to the certification required for the backflow testing and repair.  The state of Wyoming recognizes the American Backflow Prevention Association (ABPA) certification.  Will the VA recognize an ABPA certification for testing and repair in lieu of the ASSE 5110 and 5130 certification?

Answer: The SOW section 2.0 Certification covers the required certifications.

Dates listed in Section I and XIV are hereby updated to no later than 16:00pm MT, January 27, 2026.

See attached document: Backflow Survey Oct2025.

No additional Questions will be answered.